## Renew_info
name | bus | carrier | tech | profile | capacity | type
BB_wind | BB_bus_el | wind | onshore | BB_wind_profile | 265 | volatile
BB_pv_utility | BB_bus_el | solar | pv | BB_pv_utility_profile |  | volatile
BB_pv_distributed | BB_bus_el | solar | pv | BB_pv_distributed_profile | 234 | volatile
scenario 1
resource
BB_pv_distributed | 234.1 | MW
BB_pv_utility | 80 | MW
BB_wind | 475 | MW
scenario 2

## Dispatch_info
name | bus | carrier | tech | marginal_cost | original_variable_cost | capacity | type
BB_S1 | BB_bus_el | hfo | steam | 1000000 | 14.62 | 20 | dispatchable
BB_S2 | BB_bus_el | hfo | steam | 1000000 | 14.62 | 20 | dispatchable
BB_D10 | BB_bus_el | hfo | lsd | 350.0454 | 28.95 | 12.5 | dispatchable
BB_D11 | BB_bus_el | hfo | lsd | 350.0454 | 28.95 | 12.5 | dispatchable
BB_D12 | BB_bus_el | hfo | lsd | 350.0454 | 28.95 | 12.5 | dispatchable
BB_D13 | BB_bus_el | hfo | lsd | 350.0454 | 28.95 | 12.5 | dispatchable
BB_D14 | BB_bus_el | hfo | lsd | 303.1249 | 12.68 | 29.7 | dispatchable
BB_D15 | BB_bus_el | hfo | lsd | 303.1249 | 12.68 | 29.7 | dispatchable
BB_GT02 | BB_bus_el | diesel | gt | 695.616 | 65.04 | 13 | dispatchable
BB_GT03 | BB_bus_el | diesel | gt | 678.386 | 25.25 | 13 | dispatchable
BB_GT04 | BB_bus_el | kerosine | gt | 693.3112 | 72.2 | 20 | dispatchable
BB_GT05 | BB_bus_el | kerosine | gt | 693.3412 | 72.2 | 20 | dispatchable
BB_GT06 | BB_bus_el | diesel | gt | 644.3304 | 72.2 | 20 | dispatchable
BB_Biomass | BB_bus_el | bagasse | steam | 1000 | 18 | 25 | dispatchable
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: the actual variable costs were included here as opposed to marginal costs
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The capacity information was taken from new utility information provided by the energy division.

## tech_info_RenpGIS
name | Location/Plant | Primary fuels | Secondary fuels | Start Fuel | Scheduled commisioning date | Scheduled decommisioning cate | Max Capacity (MW) | Rating (MW) | P-Min (Operating) (MW) | P-Min (Technical) (MW) | Gross heat rate (Btu(kWh) | Heat Rate Coef (A) (Btu/KWH) | Heat Rate Coef (B) (Btu/KWH) | Heat Rate Coef (C) (Btu/KWH2) | Full Load Heat Rate (BTU/KWH) | Fixed Operational & Maintenance Cost ($/MWh) | Variable Operational & Maintenance $/MWh | Min Up Time (HRS) | Min Down Time (HRS) | Ramp Up Rate (MW/MIN) | Ramp Down Rate (MW/MIN) | Run Up Rate (MW/MIN) | Start Time (Min) | Start Cost ($/START) | Droop Setting % | Load Control Mode (KW/DROOP)
BB_pp_SG_LSD_D10 | spring garden | HFO | Diesel | HFO | 1982 | 2019 | 12.5 | 11 | 9 | 6 | 0 | 68.81 | -4113 | 0.562 | 8413 | 0 | 28.95 | 1 | 3 | 3 | 3 | 0.3 | 30 | 670 | 4 | KW
BB_pp_SG_LSD_D11 | spring garden | HFO | Diesel | HFO | 1982 | 2019 | 12.5 | 11 | 9 | 6 | 0 | 68.81 | -4113 | 0.562 | 8413 | 0 | 28.95 | 1 | 3 | 3 | 3 | 0.3 | 30 | 670 | 4 | KW
BB_pp_SG_LSD_D12 | spring garden | HFO | Diesel | HFO | 1987 | 2019 | 12.5 | 11 | 9 | 6 | 0 | 68.81 | -4113 | 0.562 | 8413 | 0 | 28.95 | 1 | 3 | 3 | 3 | 0.3 | 30 | 670 | 4 | KW
BB_pp_SG_LSD_D13 | spring garden | HFO | Diesel | HFO | 1990 | 2019 | 12.5 | 11.5 | 9 | 6 | 0 | 68.81 | -4113 | 0.562 | 8413 | 0 | 28.95 | 1 | 3 | 3 | 3 | 0.3 | 30 | 670 | 4 | KW
BB_pp_SG_LSD_D14 | spring garden | HFO | Diesel | HFO | 2005 | 2035 | 29.7 | 26 | 15 | 11 | 0 | 52.12 | 4675 | 0.043 | 7719 | 0 | 12.95 | 1 | 3 | 3 | 3 | 0.5 | 30 | 1145 | 5 | DROOP
BB_pp_SG_LSD_D15 | spring garden | HFO | Diesel | HFO | 2005 | 2035 | 29.7 | 26 | 15 | 11 | 0 | 52.12 | 4675 | 0.043 | 7719 | 0 | 12.95 | 1 | 3 | 3 | 3 | 0.5 | 30 | 1145 | 5 | KW
BB_pp_SG_S1 | spring garden | HFO | Diesel | HFO | 1976 | 2017 | 20 | 18 | 8 | 8 | 0 | 93.11 | 1913 | 0.291 | 12386 | 0 | 14.62 | 3 | 0 | 5 | 5 | 0 | 600 Cold | 28582 | 6 | DROOP
BB_pp_SG_S2 | spring garden | HFO | Diesel | HFO | 1976 | 2017 | 20 | 18 | 8 | 8 | 0 | 93.11 | 1913 | 0.291 | 12386 | 0 | 14.62 | 3 | 0 | 5 | 5 | 0 | 240 Hot | 28582 | 6 | DROOP
BB_pp_SG_SCGT_GT01 | spring garden | HFO | Diesel | HFO | 1973 | 2019 | 17.5 | 17 | 6 | 6 | 0 | 0 | 0 | 0 | 17425 | 0 | 313.18 | 3 | 5 | 0.73 (MW/s) | 0.73 (MW/s) | 1.2 | 5 | 203 | 5 | DROOP
BB_pp_GR_SCGT_GT02 | garrison | HFO | Diesel | HFO | 1990 | 2017 | 13 | 11 | 6 | 6 | 0 | 47.13 | 6428 | 0.235 | 13111 | 0 | 65.04 | 3 | 3 | 3 | 3 | 1.2 | 5 | 177 | 9 | DROOP
BB_pp_SW_SCGT_GT03 | seawell | HFO | Diesel | HFO | 1996 | 2022 | 13 | 11 | 6 | 6 | 0 | 47.13 | 6428 | 0.235 | 13111 | 0 | 25.25 | 3 | 3 | 3 | 3 | 1.2 | 5 | 177 | 9 | DROOP
BB_pp_SW_SCGT_GT04 | seawell | HFO | Diesel | HFO | 1999 | 2025 | 20 | 18 | 6 | 6 | 0 | 67.81 | 5028 | 0.132 | 11057 | 0 | 72.2 | 3 | 3 | 3 | 3 | 1.2 | 5 | 193 | 9 | DROOP
BB_pp_SW_SCGT_GT05 | seawell | HFO | Diesel | HFO | 2001 | 2025 | 20 | 18 | 6 | 6 | 0 | 67.81 | 5028 | 0.132 | 11057 | 0 | 72.2 | 3 | 3 | 3 | 3 | 1.2 | 5 | 212 | 9 | DROOP
BB_pp_SW_SCGT_GT06 | seawell | HFO | Diesel | HFO | 2002 | 2027 | 20 | 18 | 6 | 6 | 0 | 67.81 | 5028 | 0.132 | 11057 | 0 | 72.2 | 3 | 3 | 3 | 3 | 1.2 | 5 | 193 | 9 | DROOP
Dispatch in current use 2018
Summary
LSD | 6
S | 2
WH / CoGen | 2
Gas | 6
Efficiencies and losses
Generation Auxillaries | 3.8 | %
System losses | 6.38 | %
Peak Demand | 160 | MW
Average Demand | 130 | MW
Minimum Demand | 92 | MW
Annual Gross Power Production | 969.4 | GWh/a
summary table of information from the IRENA report
name | VOM costs (Bds$/MW/h) | Captical cost (BBD/MW) | Fixed O&M / 1000 BBD/MW/year | capacity (MW) | Max Avialbilty/% | efficiency (%) | historical Production (Gwh) | lifetime (years) | Feedstock
BB_pp_SG_LSD_D10 | 28.95 | 2750 | 166.68 | 11 | 83.4 | 40 | 64 | 30 | HFO
BB_pp_SG_LSD_D11 | 28.95 | 2750 | 166.68 | 11 | 83.4 | 40 | 55 | 30 | HFO
BB_pp_SG_LSD_D12 | 28.95 | 2750 | 166.68 | 11 | 83.4 | 40 | 67 | 30 | HFO
BB_pp_SG_LSD_D13 | 28.95 | 2750 | 166.68 | 11 | 83.4 | 40 | 73 | 30 | HFO
BB_pp_SG_LSD_D14 | 12.68 | 3000 | 416.6 | 26 | 87.7 | 43 | 182 | 30 | HFO
BB_pp_SG_LSD_D15 | 12.68 | 3000 | 416.6 | 26 | 87.7 | 43 | 182 | 30 | HFO
BB_pp_SG_S1 | 14.62 | 1750 | 230.52 | 18 | 86.4 | 25 | 86 | 40 | HFO
BB_pp_SG_S2 | 14.62 | 1750 | 230.52 | 18 | 86.4 | 25 | 86 | 40 | HFO
BB_pp_SG_SCGT_GT01 | 313.18 | 5000 | NA | 17 | 85.1 | 20 | 2 | 25 | Diesel-SG
BB_pp_GR_SCGT_GT02 | 65.04 | 2000 | 53.64 | 11 | 57 | 23 | 9 | 25 | Diesel
BB_pp_SW_SCGT_GT03 | 25.25 | 2000 | 41.16 | 20 | 81.3 | 22 | 25 | 25 | Diesel
BB_pp_SW_SCGT_GT04 | 72.2 | 2000 | 10.68 | 20 | 89.5 | 26 | 27 | 25 | Diesel
BB_pp_SW_SCGT_GT05 | 72.2 | 2000 | 10.68 | 20 | 89.5 | 26 | 9 | 25 | Jet A1
BB_pp_SW_SCGT_GT06 | 72.2 | 2000 | 10.68 | 20 | 89.5 | 26 | 29 | 25 | Diesel
Renewable Resources | VOM costs (Bds$/MW/h) | Captical cost (BBD/MW) | Fixed O&M / 1000 BBD/MW/year | Efficiency (%) | Fuel Cost (BBD/million Btu)
Wind | 1 | 3500 | 138 | NA | 0
Utility-scale PV | 1 | 3900 | 38 | NA | 0
Residential and Commercial PV | 1 | 5400 | 52 | NA | 0
Biomass | 15 | 7.00-10.00 | 200 | NA | 6.72
Note on G6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: this was reviewed and estamited as 30 years is the usual life span.

## Marginal_Costs
| IRP Revised Report | Energy Division |  | IRENA
name | Fuel type | VOM costs (Bds$/MW/h) | capacity | VOM costs (Bds$/MW/h) | capacity | fuel cost (1000 BB/million Btu) | VOM/ Bds$/ MWh | Gross heat rate (Btu/kWh) | Gross heat rate (mmBtu/kWh) | marginal cost fuel ohne VOC (Short-run) | full marginal cost of fuel
BB_pp_SG_LSD_D10 | HFO | 28.95 | 11 | 28.95 | 11 | 166.68 | 33.65 | 8063 | 8.063 | 290.268 | 319.218
BB_pp_SG_LSD_D11 | HFO | 28.95 | 11 | 28.95 | 11 | 166.68 | 33.65 | 8063 | 8.063 | 290.268 | 319.218
BB_pp_SG_LSD_D12 | HFO | 28.95 | 11 | 28.95 | 11 | 166.68 | 33.65 | 8063 | 8.063 | 290.268 | 319.218
BB_pp_SG_LSD_D13 | HFO | 28.95 | 11.5 | 28.95 | 11 | 166.68 | 33.65 | 8063 | 8.063 | 290.268 | 319.218
BB_pp_SG_LSD_D14 | HFO | 12.68 | 26 | 12.68 | 26 | 416.6 | 10.38 | 7456 | 7.456 | 268.416 | 281.096
BB_pp_SG_LSD_D15 | HFO | 12.68 | 26 | 12.68 | 26 | 416.6 | 10.38 | 7456 | 7.456 | 268.416 | 281.096
BB_pp_SG_S1 | HFO | 14.62 | 20 | 14.62 | 18 | 230.52 | 18.13 | 12325 | 12.325 | 443.7 | 458.32
BB_pp_SG_S2 | HFO | 14.62 | 20 | 14.62 | 18 | 230.52 | 18.13 | 12325 | 12.325 | 443.7 | 458.32
BB_pp_SG_SCGT_GT01 | N/A | 313.18 | 17.5 | 313.18 | 17 | N/A | N/A | N/A | N/A | N/A | N/A
BB_pp_GR_SCGT_GT02 | Diesel | 65.04 | 13 | 65.04 | 11 | 53.64 | 52.09 | 13276 | 13.276 | 619.9892 | 685.0292
BB_pp_SW_SCGT_GT03 | Diesel | 25.25 | 13 | 25.25 | 20 | 41.16 | 34.86 | 13276 | 13.276 | 619.9892 | 645.2392
BB_pp_SW_SCGT_GT04 | Diesel | 72.2 | 20 | 72.2 | 20 | 10.68 | 104.65 | 11134 | 11.134 | 519.9578 | 592.1578
BB_pp_SW_SCGT_GT05 | Diesel | 72.2 | 20 | 72.2 | 20 | 10.68 | 104.65 | 11134 | 11.134 | 519.9578 | 592.1578
BB_pp_SW_SCGT_GT06 | Diesel | 72.2 | 20 | 72.2 | 20 | 10.68 | 104.65 | 11134 | 11.134 | 519.9578 | 592.1578
IPR report
HFO-Base -Bds$/mmbtu (LHV)- 2016 | 36
Jet A1 -Base -Bds$/mmbtu (LHV)- 2016 | 54.75
Diesel -Base-Bds$/mmbtu (LHV)- 2016 | 46.7
marginal costs | (VOM+ marginal costs of fuel)
cal fuel cost portion of the short run marginal costs | MC= HR * F
40

## dispatchable new
name | bus | carrier | tech | marginal_cost | capacity | type
BB_S1 | BB_bus_el | hfo | steam | 1000000 | 20 | dispatchable
BB_S2 | BB_bus_el | hfo | steam | 1000000 | 20 | dispatchable
BB_D10 | BB_bus_el | hfo | lsd | 350.0454 | 12.5 | dispatchable
BB_D11 | BB_bus_el | hfo | lsd | 350.0454 | 12.5 | dispatchable
BB_D12 | BB_bus_el | hfo | lsd | 350.0454 | 12.5 | dispatchable
BB_D13 | BB_bus_el | hfo | lsd | 350.0454 | 12.5 | dispatchable
BB_D14 | BB_bus_el | hfo | lsd | 303.1249 | 29.7 | dispatchable
BB_D15 | BB_bus_el | hfo | lsd | 303.1249 | 29.7 | dispatchable
BB_GT02 | BB_bus_el | diesel | gt | 695.616 | 13 | dispatchable
BB_GT03 | BB_bus_el | diesel | gt | 678.386 | 13 | dispatchable
BB_GT04 | BB_bus_el | kerosine | gt | 693.3112 | 20 | dispatchable
BB_GT05 | BB_bus_el | kerosine | gt | 693.3412 | 20 | dispatchable
BB_GT06 | BB_bus_el | diesel | gt | 644.3304 | 20 | dispatchable
BB_Biomass | BB_bus_el | bagasse | steam | 1000 | 25 | dispatchable
Note on E1: Andre Harewood: the costs were made high so the system would ignore them and use other generators!